## HE CHP
Site Name
Applicant / Operator Company Name
Description
Type | Please Select |  |  |  |  | Voltage | For electricity exported to the grid | For electricity consumed onsite
Primary Fuel |  |  |  | Please Select | 1 | >200kV | 1 | 0.985
Electrical Rating (MW) |  | MWe |  | CCGT Heat Recovery | 0.8 | 100-200kV | 0.985 | 0.965
Thermal Rating (MW) |  | MWth |  | Steam Backpressure Turbine | 0.75 | 50-100kV | 0.965 | 0.945
Year of construction |  |  |  | Steam Condensing Extraction Turbine | 0.8 | 0.4-50kV | 0.945 | 0.925
Grid Connection |  |  |  | Gas Turbine with Heat Recovery | 0.75 | <0.4kV | 0.925 | 0.86
Useful heat demand type |  |  |  | Internal Combustion Engine | 0.75
On-site electricity use |  | % |  | Stirling engines | 0.75
|  |  |  | Fuel Cells | 0.75
Overall Efficiency |  |  |  | Steam Engine | 0.75
Electricity Generation |  | MWh |  | Organic Rankine Cycle | 0.75
Useful Heat Output |  | MWh | Net of condensate return | WTE | 0.75
Fuel Input |  | MWh
Electric Efficiency | 0% |  | Electricity Generation/Fuel Input | Steam/ Hot Water |  |  | Type of the unit - Default power to heat ratio, C
Thermal Efficiency | 0% |  |  | Direct Exhaust Gas |  |  | Please Select | 1000000
Overall Efficiency | 0% | [5 empty] | CCGT Heat Recovery | 0.95
Threshold Efficiency | 100% |  | Annex II of 2004/8/EC | Measured/Design Data |  |  | Steam Backpressure Turbine | 0.45
Meets Annex II Criterion | No |  |  | Default Power to Heat |  |  | Steam Condensing Extraction Turbine | 0.45
|  |  |  | 1000000 |  |  | Gas Turbine with Heat Recovery | 0.55
Power to Heat Ratio (measured during period of full CHP operation) |  |  |  | #DIV/0! |  |  | Internal Combustion Engine | 0.75
Measured or Default | Measured/Design Data | [5 empty] | Stirling engines | No Default Value
Heat output |  | MWh |  |  |  |  | Fuel Cells | No Default Value
Electricity output |  | MWh
Fuel Input | [6 empty] | Steam Engine | No Default Value
Cactual (measured during period of full CHP operation) | 0 | [5 empty] | Organic Rankine Cycle | No Default Value
[7 empty] | WTE | No Default Value
Electricity from HE CHP
Useful Heat Output | 0 | MWh
ECHP | 0 | MWh
E non-CHP | 0 | MWh | Total electricity - ECHP
Primary Energy Savings
Efficiency for Electricity Production |  |  | Refer to decision paper
non-CHP Fuel | 0 | MWh
CHP Fuel | 0 | MWh | Total fuel - non-CHP Fuel
CHP Hn | 0% |  | Useful heat/CHP Fuel
CHP En | 0% |  | ECHP/CHP Fuel
Ref Hn |  |  | Annex II of 2011/877/EU
Ref En |  |  | Annex I of 2011/877/EU
Grid loss correction |  |  | Annex IV of 2011/877/EU
Climate Adjustment | 0.6% |  | Annex III of 2011/877/EU, 9 C average temperature
Ref En (Adjusted) | 0% |  | Adjusted reference value electrical efficiency
PES | 0%
Meets Annex III Criterion | No
This template is provided for guidance. Applicants should ensure that operational data and calculation methods are as per 2004/8/EC and associated guidelines and reference data.
Green cells are for user entry. Blue cells are calculated.